# 5.	TECHNICAL SPECIFICATIONS

________________________________________________

  - GENERAL TECHNICAL SPECIFICATIONS  FOR WORKS ON THE EXTERNAL RAINWATER DRAINAGE SYSTEMS

All positions and estimations of the scope of work include, besides the individual description of all the items, all work, material, equipment, additional tools, expenses and the profit of the company necessary for the quality and complete finalization of the described item.

The measurement of the quantity of the effective work execution will be done according to the clauses prescribed by the "Standard Code of Practice" in Civil Engineering.

Execution of work

- Prior to the preliminary works, the Contractor has to convey the route survey, mark the route and its objects, set up the reticulation of the temporary benchmarks which will control the levels and alignment constantly during the construction works. The Contractor has no right to assign the contracted work in whole or in part to a third party without the written consent of the Engineer. Works must be carried out in accordance with these conditions and other regulations for this type of work and for sanitary inspection.  If during the work performance, some of these regulations have suffered changes, amendments or new regulations are made, the contractor is obliged to act on them without compensation.

- The material for the performance of the contracted works must correspond to JUS or other recognized regulations for this type of material. Each delivery of materials (pipes, fittings, etc.) must be delivered the certificate of compliance that it has been tested and in accordance with the regulations. The Contractor is responsible for all the built-in and extra materials and for the performed works until the final notice, i.e. obtaining the building license.

- Works must be performed according to the project, contract, and these conditions. In case there is any exception, the Contractor is obliged to present the Engineer in a timely manner with the consent of the Designing Engineer. For any eventual change, there must be a written consent of the Designer Engineer and Engineer. The contractor must arrange the works so that the material and the trenches do not interfere with the works of other Contractors at the site. The Contractor is also obliged to pay all the delays and damages that his work entails to other contractors.

- Trench excavation, bedding and compacting trench must be carried out accordingly to the project description Pipes can be laid only on the planned substrate and after checking the angle with the leveling instrument. Plumbing is permitted by the Engineer (by logging it in). When laying the pipeline, the dimension line of the bottom of the trench for each tube must be controlled by a level instrument. The pipe joints should, therefore, be made watertight. The material and the method of joining for each type of pipeline is determined by the project.  The trench backfilling shouldn’t start before the pipeline has been tested for water tightness. The laid pipeline is checked by the Engineer as well as compliance of the couplings, route, controls the side elevation of the profile provided by the contractor and allows (by logging it in) the trench backfilling. The trenches compacting is done in layers up to 30 cm, and compaction test is done at every 60 sm of height and at 20 m' of the length of the trench. To enable the backfilling and compaction in layers up to 30 cm, the formwork must be pulled out to prevent the collapse of the sides of the trench.

- If the trench is dug deeper than the projected one, the addition of the material must be in the layers with the mechanical means to be compacted to a certain compaction. In such cases the control of a compaction is mandatory.  In this case, the work and materials expense will be covered the Contractor and the Investor will not pay them separately.

- A reduction in the level in case of occurrence of any underground, atmospheric or water of any another origin shall be carried out in a required method. Pipes can be laid only in trenches without water.

- The obligation of the Contractor is to secure installations and objects from mechanical damage, clogging, illegal use and the like until the final note, i.e. obtaining the inspection certificate.

- Testing and discharging of the inlet can only be carried out with the consent of the Engineer. It is forbidden to empty the inlet into the excavated trenches. All costs for processing joints or repairing improperly executed works are covered by the Contractor.

- The contractor is obliged to do all the works (with the provision of necessary materials) that are not covered by the project if they are necessary for the normal functioning of the installation or compliance with existing regulations. The contractor must submit the proper installation for required operation.

- At points of crossing with other installations, security must be ensured from collision or subsequent damage during exploitation.

- The contractor is obliged to provide land registry survey of installations and to call the registry representative on time (before the backfilling) to perform the survey.

- The contractor is obliged to supply the pipelines with facilities on them to the Engineer for use and maintenance and to submit a written document about it.

  - CALCULATIONS AND PAYMENTS OF WORKS

Works on the water supply and sewage systems are all to be done in accordance with the project, whose part is a specification of the materials, estimation of the scope and all necessary details and drawings. The works should be carried out with the approval of the Engineer, without which no changes can be made as well as more important phases carried out (e.g. trenching, testing of pipes and installations, etc.). The unit prices of these works positions include:

a)	All necessary preliminary and final works which require quality and fully- completed work.

b)	All expenses for completion of the works and required for: labour, a material with scaffolding, tools, formworks, and scaffolds, fittings, installation costs, transport, directing as well as all other expenses according to the valid regulations for forming price.

c)	The Contractor shall, at his own expense, inspect the pipes, installations and sanitary facilities according to the existing technical regulations: the plumbing shall be tested at the pressure determined by the Engineer, and the sewage with the pressure increased for 4m.

The Contractor is obliged to disinfect all pipelines, water pipes, and water analysis after the work is finished at his own expense, which will be stated in the construction logbook, and the documentation on the water analysis should be attached to it, after which the technical inspection and reception of works can be performed.

It is mandatory to compile a commission record on water and sewage testing in the presence of the Engineer.

d)	d) Excavation costs include excavation of trenches with parallel vertical cut-off of the sides and bottom of the trunk, all extra works to prevent collapse and atmosphere water, atmospheric or groundwater extraction, excavation and embankment planning, bedding, grounding in layers from 20 to 30 cm, transport of the remaining land (up to 100 m) with spreading, and in a place approved by the Engineer, compacting and planning it, marking trenches and other.

e)	Measurement and expenses for the concrete will be made to the lines indicated in the drawings, and in the manner described in these conditions.

When measuring for the expenses of the concrete, all openings with a cross-section area larger than 400 cm2 will be rejected.

The compensation for the concrete will be done per cubic meter according to the unit prices offered in the calculation. These unit prices shall include labour costs, all materials, machinery used, platters and scaffolds and all other direct and indirect expenses that must be incurred in order to carry out the operation of the offered positions, and in accordance with the provisions of these technical conditions, regulations, and standards.

The unit prices of reinforced concrete will include a layer of 5 cm thin skin of the brand MB15, which will be laid on surfaces that are not sufficiently firm and flat, and to be used in concrete with reinforced concrete.

By measuring and paying for the position: the supply and installation of concrete iron, only those weights of concrete iron that are actually installed in concrete and in accordance with the reinforcement plans will be covered.

Payment for the supply and installation of concrete iron will be done per kilogram or per square meter if it is a reinforcement network, and according to unit prices in the invoice. These unit prices will include the cost of procurement and transport of concrete iron, binding wires, pads and other materials required, cleaning, cutting, bending, assembly, welding and all other costs related to the supply and installation of concrete iron.

The unit price offered per tonne or kilogram for concrete Ø12 mm diameter will also include rods of Ø12 mm diameter.

All works must be executed as planned in the Project, according to technical regulations and standards with a high-quality material and labour and tested according to the existing regulations.

Low-quality material that doesn’t comply with technical regulations, shall be removed from the construction site by the Contractor, that is, to install quality materials instead at his own expense, without any compensation..

If works are performed with material that does not comply with the technical regulations of the project or the instructions of the Engineer, the Contractor is obliged to perform these works again with quality material at their own expense, without any compensation.

If the project documentation is incomplete or inaccurate, the Contractor is obliged to timely, and prior the works, request supplementation or necessary interpretation of the project documentation from the Engineer. The necessary modifications or demolitions that would result from the failure to fulfil the stated obligations of the contractor in terms of the project, shall be borne by the Contractor without the right to compensation and extension of the deadline.

The Contractor is obliged, after executed works, or according to the instructions of the Engineer during the individual phases of the works, to bring the facility to the proper state of use, as well as to close and grade trenches and holes, to clean all objects, installations and devices and parts.

The Contractor is obliged to preserve all constructed and installed objects, installations, devices and parts in the proper clean state until handover and provide the necessary security. This is included in the unit price.

  - HYDRAULIC TESTING OF THE SEWAGE RETICULATION

When constructing a sewage system, it is necessary to test the built network, as is the case with the water supply system, in order to check the quality of the performed works.

Excessive infiltration of water into the network (external water entrance), as well as exfiltration (loss of the foul water from the pipe to the ground), must not be allowed. Both phenomena can lead to instability of the building, and the leakage of dirty water into the terrain can have consequences from a sanitary point of view.

In order to ensure the necessary water tightness of the sewage system, it is required for the pipes (ducts) to be waterproof, and the couplings should be made watertight under certain conditions.

In a well-executed sewage system, there should be neither filtration nor exfiltration.

The quality of the couplings and the pipeline is checked as follows:

a) in the ground with groundwater - when water penetrates into a pipeline at a natural level of groundwater, if the groundwater level is 2-4 m above the tube's circumference, the amount of water caught in the pipe should not be higher than the values ​​indicated in the table number 1. For a groundwater level higher than 4 m, a permissible amount of water perpendicular to the perimeter of the tube is increased by 10% for each subsequent meter of the increased slowdown (over 4 m).

b) in dry terrain - when water is leaking from the pipeline to the ground. To perform this test, a part of the sewage pipeline between the shafts is filled with water up to 4 m above the hub top. In the upstream shaft, the loss should not exceed the values ​​given in Table 1.

c) in the ground with lower groundwater - where the groundwater level is less than 2 m above the tube's head, the loss of water from the tube is tested. The test shall be carried out the same as under (b).

Checking the sewerage system for water tightness is done before the pipe is sealed in the trench. In the ground with high groundwater, the test is done by measuring the amount of water that flows into the sewage, on the overflow which is placed in the trench at the downstream manhole.

In dry terrain, measurement is done in two ways:

a) The first way is to simultaneously test two adjacent sections for three inspection shafts. At the final downhill, the system is sealed (closed), and through the middle inspection shafts, trenches are filled with water to a certain level. Then, the couplings are tested for water tightness and maintenance of a constant water level in the shaft is performed for 30 minutes.

The permitted quantities of water infiltration or leakage exfiltration the couplings and walls of the sewer pipes are given in the following table.

TABLE   No. 1

The allowed amount of water infiltration or exfiltration in m3 / (24h x km)

length of the pipeline of a given diameter in mm

Do:

| polyester pipes |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Regarding the use of these data, one should bear in mind the following:

1. For concrete and reinforced concrete pipes with a diameter greater than Ø 600 mm, the allowed quantities can be obtained by increasing the amount by 10% for each subsequent decimetre (e.g. for Ø 700; 23 + 2,3 = 25.3 m3 / (24h x km).

2. For the construction of a brick collector or similar material, the allowed quantities must not exceed 10 m3 / 24 h per km of length, regardless of the size of the profile.

3. For collectors of prefabricated and reinforced concrete elements, the permitted inflow or loss of water is taken the same as for reinforced concrete pipes, which have the same cross-sectional area.

4. The permissible amount of incoming or lost water through the walls and bottom of the shafts at 1 m of their depths is taken to be the same as for losses or inflow of water on a 1m length of pipe of the same diameter, such as a manhole.

5. When testing a larger diameter pipeline of Ø 1000 mm and a larger cross-section of 1 m2 that goes through an undeveloped territory (where water is difficult to handle), the test is carried out only on one approved section.

6. Testing of the pipeline on water tightness must be done only 24 hours after charging the system.

The loss of water is calculated per amount of water that is the amount of water that is poured for 30 minutes per 1 km, and then the conversion is done for 24 hours.

REPORT

ABOUT PERFORMED HYDRAULIC TESTING OF SEWER SYSTEM FOR WATERTIGHTNESS

I)	Data:

- Name of the object

- Section - stretch No.			from				to

- Manufacturer of pipes

- Material type

- The trench dimension (with thickness of the wall)			______

- Kind of joining and joints number

- Materials quality certificate

- Altitude difference between the highest and lowest test points		______

- Date and time of testing

II)	Testing:

1. Time difference in hours (from the end of the charge to the beginning of the test)

2. Amount of the added water								______

3. Note about testing (pressure on couplings, on revision backdrops, etc.)

The tested section is correct - faulty, so hydraulic testing is not required - it should be repeated.

Repair is done

The carried out section of the sewage from    to       is considered to be correct on the basis of the above tests, and it is allowed to be backfilled.

Annex: The situation of the tested stretch with the dimension lines of the bottom of the trench.

FOR CONTRACTOR:						FOR INVESTOR:

_______________________		                                         ______________________

  - GENERAL TECHNICAL REQUIREMENTS FOR POLYESTER PIPES

Polyester pipes are made from polyester resin reinforced with glass fibers. Combining glass fibers of thermostable polyester resin and special fillers in recommended proportions, pipes with a wide range of physical and chemical features can be produced.

The official marking for the specified piping is RTRP but they are generally related to as fiberglass pipes, a fiberglass reinforced plastic, glass reinforced plastic etc.

Standardization is adherent to American Society for Test and Materials (ASTM) as follows:

Specifications and classifications of products:

ASTM D 3262 (2006) – Standard specification for fiberglass sewage pipes (thermoactive resin reinforced with glass fibers). It is applied for sewer pipes with or without the silicate sand and polyester or epoxy resin.

ASTM D 3517(2006) – Standard specification for fiberglass pipes (thermoactive resin reinforced with glass fibers). It is applied for pipes with or without the silicate sand and polyester or epoxy resin.

Standard procedures:

Dimensions:

ASTM D 3567(2006) – Standard procedure for determining pipes dimensions and fittings from reinforced thermoactive resin.

Visible effects:

ASTM D 2563 (2006) – Standard procedure for classification of visual defects in laminated parts of glass reinforced plastics.

Installation:

ASTM D 3839 (2008) – Standard procedure for underground installation of flexible pipes made of reinforced thermoactive resin and reinforced plastic pipes.

Note: Standards relating to test methods and all other standards can be found in the manufacturer's manual.

Physical and chemical characteristics

Bearing capacity and weight ratio. Polyester piping systems have excellent bearing characteristics in relation to their weight. In this respect, they exceed iron pipes as well as those of carbon and stainless steel.

Low weight. Fiberglass composites have a low weight. Polyester piping systems are only 25% of the weight of the respective steel tubes and only 10% of the corresponding concrete products.

Electrical conductivity. Standard polyester pipes are not conductors.

Stability of dimensions. Polyester pipes remain within the limits of the critical tolerances that are required when used in the most difficult installation conditions.

Low maintenance cost. Polyester pipes are easy for maintenance, they are not corroding and are easy to clean. They require minimal protection against the effects of the environment.

Chemical resistance.  Depends primarily on the material used, the resin and the glass fibre. Other factors may also affect the laminate resistance, such as the liner construction, hardening, the method of manufacture and the method of installation. The effect of temperature and stress on laminates must also be taken into account.

The choice of resin is based on the knowledge how it will behave when used in a particular chemical environment. Information related to the technical process of obtaining the product should also be inspected. Polyester pipes are resistant to many types of corrosion: galvanic, aerobic, corrosion when drilling openings, graphite and intergranular.

The polyester pipe is susceptible to chemical corrosion by hydrolysis, oxidation, pyrolysis or under the action of a solvent. Sensitivity depends on the type of resin and environment.

Temperature resistance.  This resistance depends on the resin matrix from which the pipe is made. The upper limit of the working temperature depends on the chemical environment and the load of the pipe system. For the specific performance of a specific type of resin, at higher temperatures, the manufacturer should be contacted.

Flammability. The flame-retardant performances of the polyester pipes are noticed on the resin systems containing halogens or phosphorus. Hydrated fillers can increase resistance. Other additives, primarily antimony oxides, increase the efficiency of halogen compounds. It should be noted that all thermoactive resins are organic materials and in the certain combination of heat and oxygen, every organic substance is flammable. For more information on flammability, please consult the manufacturer.

Weather resistance. Most thermoresistant resins used in the production of polyester pipes are prone to degradation under ultraviolet (UV). This degradation occurs mainly on the surface but does not impair the structural integrity of the pipe. The addition of pigments, dyes or UV stabilizers into the resin system or the dying of exposed surfaces significantly reduces their degradation.

Abrasion resistance. Polyester pipes can be manufactured for use under strong abrasion conditions by coating the product with sand, silicon fluoride, carbon dioxide, ceramic beads or tiles. The material used for coating should correspond to the hardness and abrasiveness of the contents to be transported through the pipe.

density						1,75 – 1,80g/cm3

the module of elasticity				25 – 30 GPa

tensile strength (circular)			60 – 400 MPa

tensile strength (axial)		 		40 – 50 MPa

bending strength (circular)			140 – 500 MPa

elongation to the breaking point		1.5 – 2.0 %

coefficient of linear expansion			25 – 30 10-6 l/oC

max temperature of transported medium	50oC

coefficient of temperature conductivity		0.3 – 0.35 W/mK

Hydraulic characteristics

Absolute roughness		k = 0.012mm

Hazen – Williams constant	C = 150

Manning’s constant		n = 0.0095 – 0.012

Pipe Diameters

Pipe Diameters

Polyester pipes can be delivered with the following nominal diameters (mm):

300, 400, 500, 600, 700, 800, 900, 1000, 1200, 1400, 1600, 1800, 2000 and 2400mm.

Pressure classes

Polyester pipes are delivered in the following pressure classes:

| MARKING | OPERATING PRESSURE |
| --- | --- |
| PN | (Kpa) (bar) |
| 1.0 | 100 1.0 |
| 2.5 | 250 2.5 |
| 6.0 | 600 6.0 |
| 10.0 | 1000 10.0 |
| 16.0 | 1600 16.0 |

Pipes for operating pressures greater than 16 bars can be supplied additionally.

Classes of rigidness

The rigidness of the pipes is the ability to take over the load from the ground and traffic as well as negative internal pressures. Polyester pipes are delivered with the following tangential initial rigidity (STIS) EI/D3:

| MARKING | RIGIDNESS |
| --- | --- |
| SN | (Pa) |
| 1250 | 1250 |
| 2500 | 2500 |
| 5000 | 5000 |
| 10000 | 10000 |

The rigidness of the pipes is chosen according to:

- compaction of natural soil (number of hits per Proctor)

- the thickness of the overhead above the pipe's head

- the type of material for backfilling

- negative pressure in the pipe (in case it exists)

- traffic load

Lengths

Standard lengths of polyester pipes are 6.0 and 11.80m.

Pipe storage

It is desirable to hold pipes on flat beams, which aids placing and removing belt loops around the pipe.

Joining pipes

Polyester pipes are joined in one of the following ways:

double-ended polyester coupling

It consists of one piece of pipe material with a gutter seal at both ends. It merges in such a way that the pipe enters the coupling by pressing the sealing ring and securing sealing at the ends. The construction of the hinged joint is similar, except that the socket forms an integral part of one end of the pipe, and the tilted part is an integral part of the other end. The thickness of the pipe can be increased in the coupling zone. For an upright connection, there is a construction with one and two sealing rings (for larger pipe diameter).

mechanical steel couplings

These couplings can be used both to connect pipes as well to perform repairs. The couplings consist of a steel sheath with an inner rubber slide seal. There are three types of couplers: with a steel epoxy or PVC coated sheath, with a stainless steel sheath and a heat-galvanized steel sheath. Steel couplings that are buried often require special anti-corrosion protection in the form of polyethylene coatings or the like (as requested by the manufacturer).

butt joint

It is made of glass fibres and polyester resin and is used in situations when it is necessary to withstand axial-tensile stresses e.g. for underwater pipelines and discharge sewage pipelines. This coupling requires controlled conditions and well-trained workers.

flange

The following manners of joining are recommended:

- for sewage disposal system: polyester couplings

- for water supply system: metal couplings

- for plumbing/disposal installations: butt joints or flange.

- THE POLYESTER COUPLING

The polyester coupling is two-side sliding joint made of glass-fiber reinforced polyester.

It comes with rubber sealing rings and a certain number of pipe stoppers to ensure the correct position of the pipes and sleeves.

Three factors are essential for the effective sealing of the polyester coupling:

- bell and spigot coupling

- compaction

- wedge-shaped gutters

Polyester fittings

Polyester fittings are made of piping segments. They are delivered in the same class of pressure as the pipes.

Pipes installation

Check with manufacturer for pipeline installation instruction.

The polyester pipe is so constructed that it uses both the bedding and the backfilling zone around the tube as a support. Well-compacted grain soils are ideal for backfilling these pipes ( proved in practice). Backfilled polyester pipes allow deformations of 4 - 5% in the long run, without any structural damage.

Making trench

The trench must be wide enough to secure the compacting of the material to fill the pipe area and to ensure the proper positioning of the pipe.

| PIPE DIAMETER | A |
| --- | --- |
| DN(mm) | (mm) |
| 300 | 150 |
| 300 - 500 | 200 |
| 600 - 900 | 300 |
| 1000 - 1600 | 450 |
| 1800 - 2500 | 600 |

A – minimum width from the side of the excavation (for the trench) to the pipe.

Bedding

The pipe bedding should be made of a suitable material to ensure even and continuous support of the pipe.

Backfilling material

The pipe bedding should be made of a suitable material to ensure even and continuous support of the pipe. The material from which the polyester pipe is made has a relatively low modulus of elasticity, so that the control of the deflection of the pipe diameter, when installed, is the most appropriate indicator of the efficient functioning of the pipeline during exploitation. The deflection of the pipe must not exceed 5% of the nominal diameter. Curvature, settlement or other deformation of the pipe wall are not permitted.

Rigid joints

At places where the pipe passes through the wall, it is surrounded by concrete or a flange-bound pump, valve or something else, large bending forces may appear that act if a differential shift between the pipe and the rigid joints occurs.

For all types of rigid joints, the one who installs it must take care of the following to minimize the impact of strong forces on the pipe:

where it is possible to pour the concrete over joint, as in Figure 1, so that the straight pipe outside the concrete can be completely freely moved (the joint has a coating that reacts with fresh concrete and creates an impermeable bond)

if it is impossible to perform the previous, it is necessary to wrap the standard rubber band around the pipe, before filling the concrete, so that it "sources" out of concrete (about 25mm).

it is necessary to install the pipeline so that the first pipe section of the rigid joint is shorter:

min less from 1.0m or 1 xD

max less from 2.0m or 2 xD

Special attention must be paid to the compacting of the bedding material, in the joint zone of the pipe and the object, in order to minimize the curving.

Standards

OWENS CORNING technology of production of reinforced polyester pipes is the most modern one in this area. With the application of the mentioned technology, the constant high-quality level of products is guaranteed.

The quality assurance entails control of input raw materials and control of finished products.

The methods under which controls are carried out are according to the following standards :

ISO

ASTM

AWWA

DIN

  - SPECIAL ANNEX

on the applied prescribed measures and criteria

OBJECT:		SEWAGE SYSTEM

LOCATION:	FERATOVO POLJE

INVESTOR:

PROJECT ORGANIZATION:	CESTRA

CONTENTS:

1.	Dangers and hazards that can occur when using sewage installations

2.	Required measures for the elimination of dangers and hazards in the use of sewage installations

3.	General notices and obligations

4.	Conclusion

1.	DANGERS AND HAZARDS THAT CAN OCCUR WHEN USING SEWAGE INSTALLATIONS

-	Incorrect dimensioning of the sewage network,

- 	Insufficient slopes in the sewage network,

- 	Incorrect running of the sewage network,

- 	Incorrect number and arrangement of the inspection shafts,

- 	Incorrect choice of materials,

- 	The possibility of land pollution,

-	Danger due to crossing roads,

- 	Improper hydraulic calculation.

2.	REQUIRED MEASURES FOR THE ELIMINATION OF DANGERS AND HAZARDS WHEN USING PRIMARY AND SECONDARY SEWAGE INSTALLATIONS

-	Slopes in the sewer network are proportionate,

-	Correct running of the sewage network,

-	The correct choice of materials,

-	Correct dimensions of the sewage network,

-	Choice and arrangement of the inspection shafts is correct,

-	Inspection shafts are according to regulations,

-	Ladders in the shafts as required,

-	The internal processing of the installations is properly selected, so there is no possibility of leaking and pollution of the surrounding land,

-	The hydraulic calculation is carried out correctly.

3.	GENERAL NOTICES AND OBLIGATIONS

-	- The company that performs the works is obliged to do a special report on the organization of the site and the work on the construction site,

-	- The company that performs the works is obliged to inform the competent body of the labor inspectorate about the beginning of its work 8 (eight) days before commencement of work.

4.	CONCLUSION

The project foresees all necessary measures for the elimination of dangers and hazards in use of installations.

  - TECHNICAL REQUIREMENTS FOR  PERFORMING WORKS ON EXTERNAL INSTALLATION OF RAINWATER SEWAGE

    - PRELIMINARY WORKS

      - MARKING

Works Description

Marking of the route. Prior to initial works execute the topographic survey of the route as well as of the other relevant objects.

Measurement and Method of Payment

Paid per m' of the total surveyed route.

    - EARTHWORKS

Introductory notes

Open excavation works include:

    - excavation of the trench with the appropriate method, according to the geomechanical characteristics of the soil, with loading and removal;

    - securing the sides of the trench;

    - drainage of foul and ground waters.

The works are executed according to approved and certified:

a) 	main or execution project (in the following text: project) that includes corresponding longitudinal and transverse profiles with dimension lines and required dimensions and

b) 	project of building an organization that defines: the method of excavation including types of machines and equipment, an organization of logistics, technical solutions and approvals for all insurance and security in the site area.

The excavation will be performed according to the slopes and dimensions indicated in the project or to the levels and dimensions approved by the Engineer.

The excavation of the trench for laying pipelines can be done manually and mechanically. The width of the trench is conditioned by the diameter of the pipeline and is at least 0.80 m. The bottom of the trench must be carried out with an accuracy of + - 5 cm. For larger depths of burial, over 1.0 m, a trunk subframe should be foreseen if the terrain stability requires it.

Among other things, the project of the construction organization should provide for the turnover of traffic (on buildings in urban areas) to the unoccupied part of the road. Access to all buildings in the event of fire, the rescue of people, delivery of goods and the like must be ensured. The contractor is obliged to take measures and provide the conditions that established traffic regime near the construction site does not disturb longer than the approved deadline. The material and other consequences of this traffic disturbance shall be at the expense of the contractor if the measures, procedures, and construction dynamics are not followed during the construction process.

The contractor for the construction of installations is obliged to anticipate and harmonize all accompanying works, whether performed by them or performed with the help of other contractors.

The Contractor is responsible for the continuous harmonization and execution of:

a)   main works on installations and

b)   supporting works - relocating all kinds of installations, securing objects, restoring the original state and more.

When excavating the trench, the Contractor must take into account the possible traffic flow that may cause trenches collapse and risking workers' safety. The contractor is obliged to implement special measures for complete work safety on all stretches of excavated trenches.

If excavation is carried out in the zone of existing installations (electricity, TT, gas pipelines, heat pipeline, as well as water and sewerage), and their routes are not determined on the ground, before the beginning of work on the route, the position of these installations by transversal excavation must be determined. The detected installations shall be topographically surveyed and data submitted to the organization that maintains these installations or make the reconciliation of existing and projected installations. On the tested sections, excavate the trenches according to the adopted method, and after the approval of the Engineer.

Regardless of the requirements for which the Contractor must obtain approval for each work plan, the mechanization arrangement and the manner of progress, the Contractor is solely responsible for the method of work, quality performance of the work, completion of work within the agreed time, as well as for the safety and protective measures during the execution of the works.

These technical conditions prescribe only the most important items that specify the method and the quality of excavation work. For everything else that is not specified here, the relevant technical requirements, standards, regulations, and policies apply.

This description has adopted the unique categorization of the land, as an "excavation in soft" and covers all excavations in the soil, clay, rubble, gravel, fissured rocks and other similar materials in which the Contractor can perform the excavation using mechanization and manually. The excavation in the soft includes all the stones and solid blocks that are naturally occurring material but do not exceed the volume of 0.75 m3.

The categorization can be agreed upon at the excavation by the field book with the mandatory presence of Engineer - geomechanic. An engineer - geomechanic must inspect the bottom of the excavated trench and verify it by entering it in the construction log.

Supporting and reinforcing a work profile

The contractor is obliged to perform the supporting and reinforcement of excavated areas of the trench as required by the project and as prescribed by these conditions.

The Contractor is obliged to warn the Engineer if he considers that the approved type of barrier does not comply with the conditions of the ground, and the Engineer is obliged to check within 12 hours and, possibly, approve the request for the change of the barrier.

The Contractor is responsible for the stability of the facilities and safety at work, and if there is a risk of miscarriage, he/she must take appropriate insurance measures.

The Contractor is obliged to control, maintain and reconstruct the barrier, if necessary or on request of the Engineer.

Depending on the geotechnical and hydrogeological conditions, the assessment will be done to determine the type and strength of the barrier and the maximum time allowed from the moment of the excavation to the installation of the barrier.

Embedding works around and above the pipeline

Embedding works include:

a) 	Importing material from the dump of the excavation site or borrowing pit

b) 	Pouring the material into the trench according to requested installation procedures.

Filling works on the remaining part of the trench shall be performed in accordance with the specifications given in this chapter, or according to the drawings or orders of the Engineer.

The interspace between the pipeline and the wall of the excavated trench is embedded in the sandy material in layers of thickness up to 25 cm with compacting. The layers are applied and compacted with mechanical or other approved methods, alternately from the left and right side of the pipeline. The compaction of the embedded section must correspond to the prescribed conditions of compaction (especially on the sections of the roads), and especially on the sections in the green belt.

The construction of the embankments above the pipeline is carried out by laying in layers that are not more than 25 cm, with adequate machine compaction. The filling material is taken from the excavation site or borrowing pit if it meets the conditions of the prescribed compaction. Only inorganic material that does not contain humus and sludge ingredients can be used.

The filling on the sections of the road will be done by sand or gravel, according to the requirements for the reconstruction of the paved road. The deposited layer must be spread in the longitudinal direction along the entire width of the trench and immediately compacted.

The control of the compaction of the filler material should be carried out regularly with the registration of the test results.

The compaction of the embedded material must correspond to the prescribed conditions of compaction, both in the part of the roads and in the green belt.

Removing the extra material from the excavation site.

Dumping of the material from the excavation site includes loading, transport of excavated material to a landfill approved by the Engineer, unloading of materials with planning at the landfill.

      - MACHINE AND MANUAL TRENCH EXCAVATION

Work Description

Excavation of the trench refers to the excavation of a width less than 5 meters on the surface of the terrain, in one direction. Excavation refers to the excavation of foundations, ducts, and trenches for pipe laying.

Mechanical and manual excavation of trench in the third category material for pipe laying. The width of the trench is shown in the corresponding graphic attachments for pipe installation in accordance with the excavation and depths from the longitudinal profiles. The excavation will be strictly in line with the drawings, technical regulations, and instructions of the Engineer. The sides of the trenches must be properly cut off, and the bottom of the trench is finely planned with a drop in the project. With the excavation of the ground, dispose the ground at least 1 m from the edge of the trench.

Measurement and method of payment

Measures are given in the m³ of the excavated material in its raw state. The calculation is based on cross-sections of the terrain surveyed before and after the excavation (in accordance with the project) and approved by the Engineer. The cross-sections will be applicable for payment only after the Authorization and Signature of the Engineer.

It is paid per m³ of excavated material in its raw state.

      - TRANSPORTATION OF THE EXCAVATED MATERIAL

Work Description

Transport extra excavated material to the landfill. The price includes loading, transport, unloading and rough spreading of materials by landfill (up to 20 km), approved by the Engineer.

Measurement and method of payment

It is paid per m³ of the transported material.

    - ASSEMBLING WORKS

      - SUPPLIES, TRANSPORT, AND ASSEMBLING OF POLYESTER PIPES

Work Description

Acquisition, transport, and installation of rainwater drainage pipes and fittings for the bridge. Pipes are made of unsaturated polyester resin (GF-UP) resin, with elastic coupling elements for connecting bridge drain to a horizontal pipe distribution. Pipes are diameters:

Ø250mm

Ø300mm

Measurement and method of payment

It is paid per m' of completely installed piping depending on the radius.

      - STEEL RACKS FOR POLYESTER TUBES  (BRACKETS)

Work Description

Production of steel brackets for polyester tubes. The price includes the manufacture and installation of underlay plates, screws, clips, and brackets. Calculation per piece.

Products quality and quality assurance are specified in accordance with the following standards:

DIN 1055 (2005) and DIN 934 (bearing rods and linkages)

ISO 7093 (2000), DIN 9021 (pads and clips)

DIN 17440 (1996) and DIN 267/11, ISO 3506 (steel standards - 2009)

Measurement and method of payment

It is paid per installed piece of the rack.

    - CONCRETE WORKS

General requirements

The requirements of this chapter relate and will be applied to all concrete and reinforced concrete, which will be used for the execution of the works that are the subject of this project documentation.

Standards

The quality of the concrete and its components must comply with the requirements of the following technical regulations and standards:

a) Rulebook on Technical Measures and Requirements for Concrete and Reinforced Concrete (hereinafter PBAB);

b) Yugoslav standards (hereinafter JUS).

The contractor will obtain and keep on the construction site a copy of the standards stated in these technical requirements.

Testing of concrete and its components

All preliminary and control tests of concrete and all its components, as defined by these technical requirements, will be performed by the Contractor.

To this end, the Contractor will build a concrete laboratory and equip it with all the necessary devices, instruments and inventory necessary for the testing of concrete in the manner and scope as required by these conditions, or for the engagement of a professional organization registered for this type of activity. The selection of such professional organization shall be performed by the Contractor, with the consent of the Engineer.

The log of concrete works

During the entire construction work, the contractor is obliged to keep a log of concrete works.

The entries of the logbook of concrete works are at least:

a) data on the delivery of cement at the site:

- the name of the cement producer,

- the amount of cement and the date of arrival at the site,

- the place where the cement is stored.

b) Data on the delivery of additives to concrete

c) results of all previous and control tests of concrete, its components and additives to concrete

d) data on air, water, cement, aggregate and concrete temperatures, air humidity and weather

e) data on the start and end time of the concreting of individual objects and the timing of the installation or removal of the formwork

f) Instructions and Remarks by Engineers.

In addition to the above mentioned, the concrete works logbook will also include all other necessary data for which the need arises. The contractor will deliver one copy of the concrete works log to the Engineer.

Costs of preliminary and control tests of concrete, its components and additives to concrete, whether done at the construction site or in any other professional organization, will not pay separately to the Contractor but will include them in the unit prices of concrete offered in the pro forma invoice.

CEMENT

General requirements

For the production of all types of concrete, normal portland cement PC 35 will be used.

It is not allowed to use different types of cement, nor use the same type of cement produced by various manufacturers, in the same concrete element.

Cement must match the quality required by the Yugoslav standards for portland cement.

If the results of the control tests show that the cement has the required quality, the Engineer will allow the use of the tested delivery of cement. Otherwise, such cement will be discarded and the Contractor will replace the rejected quantities with the correct cement at their own expense, without any right to compensation.

If some amount of cement is lying longer than 3 months in the warehouse, a re-examination of this amount of cement will be carried out, regardless of the fact that it has already been tested after reaching the site.

The contractor will acquire cement, deliver it to the site and store it. Cement expense, transport, storage and all works related to manipulation with cement will be covered by unit prices of concrete in the calculation.

CONCRETE ADDITIVES

General requirements

Concrete additives must comply with the provisions of Articles 28 to 30 and 132 PBAB (1987). When producing all concrete (except for concrete brand 15), an additive for concrete suppression will be added.

The additive will be received based on the manufacturer's quality certificate proving that the additive complies with the required standard. The approval of the Engineer for the use of the additive, given on the basis of the quality certificate, shall not set free the contractor of liability if the additive does not correspond to the required quality.

The number of additives added to the concrete will be such as to ensure that the amount of air in the freshly mixed concrete is not less than 3.5% and not more than 6% relative to the volume of concrete when the aggregate is larger than 40 mm.

The additive solution will be added to the mixture in proportion to the amount of water added in the production of the concrete. Add the additive to a special device that allows the exact dosage.

The contractor will obtain the additive, transport it to the site and store it. Additives expense, transport, storage, testing and all other work related to the use of additives will be included in the unit prices of concrete in the calculation.

AGGREGATE

Stone aggregate to be used for producing concrete must be sufficiently sturdy and stable, must not contain clay and organic ingredients or other harmful admixtures for concrete as a percentage higher than allowed. According to its petrographic composition, the aggregate must not contain minerals that would influence the process of concrete hardening or the stability of concrete volume. For the hardening of concrete, a natural aggregate (gravel) obtained from the deposit and crushed stone obtained by crushing stone from an approved quarry will be used.

Before the approval of the Engineer to use the aggregate from a borrow pit, the contractor is obliged to carry out all necessary preliminary tests which will prove the required quality of aggregates and the amount available at borrow pit.

The quality of concrete aggregates must comply with the provisions of Articles 6 to 20 and 178 to 180 of PBAB (1987).

Based on the results of the test of the stone aggregate, the Engineer will decide whether the tested aggregate can be used for concrete production.

During the work, the contractor is obliged to perform regularly, i.e. at the request of the Engineer, the control of the aggregates on the construction site.

WATER

Water used for the preparation and care of the concrete has to be pure, without any organic and/or inorganic ingredients that could be harmful in process of hardening of concrete.

The quality of water for mixing the concrete has to be according to the clauses of the articles from 25 to 27 PBAB (1987). The contractor is obliged to carry out a preliminary examination of the quality of the water, and the Engineer will grant the approval for the use of the tested water on the basis of the results.

CONCRETE PRODUCTION

The concrete production will necessarily be done mechanically with the weighting of the components.

The dosing device has to be precise, controlled on a regular basis and calibrated by an authorized institute.

The mixer should have a signalling device that ensures the same mixing time. The contractor will perform the regular control of mixing by taking concrete samples at the beginning and at the end of the discharge of the mixer.

Mixing time will be determined at the site and the optimal time for good mixing of concrete, which should not be shorter than 1.5 minutes, will be determined. The speed of the mixer is prescribed by the manufacturer and is not allowed to be changed.

Additional mixing of the cement outside the concrete factory is not allowed, except in truck mixers during transport. Also, the subsequent addition of water to concrete is not permitted.

PERMISSIBLE TOLERANCE FROM PROJECTED DIMENSIONS OF CONCRETE FACILITIES

The purpose of this article is to determine the tolerances of the dimensions of concrete objects where objects can still correspond to their constructive purpose, or to the purpose of operation and exploitation. Deviation from the established directions, angles and dimensions will be allowed within the limits set here. The engineer reserves the right to reduce the tolerance described herein if such tolerances deteriorate the functionality of the facility. If the tolerances described in this article do not include individual objects, the tolerances will be determined in accordance with this article.

The Contractor shall be responsible for placing and maintaining the formwork in such a way that the dimensions of the concrete structures are maintained within the limits of the permissible tolerances described in this Article. Concrete objects whose dimensions exceed the permitted tolerance limits will be repaired and/or removed and re-concreted.

All costs of repairs or demolition and re-concreting of such facilities shall be borne by the contractor, without any right to remuneration.

Tolerance of dimensions of concrete objects:

a) 	deviation from the determined direction					 25 mm

b) 	deviation from determined dimension lines				 10 mm

c) 	variations in the dimensions of cross sections of columns, slabs, walls

and similar parts of the building							- 5 mm to +10 mm

d) 	variations in the dimensions of the footing base	 ± 10 mm

e) 	 allowed eccentricity 2% of width but not more than 20 mm

f) 	deviation of footing height 3% from the height

g) 	variation of the size and position of the openings in the walls		- 5 mm to +10 mm

At its discretion, the Engineer may grant twice the tolerance

CEMENT TECHNOLOGY STUDY

The contractor is obliged to perform a concrete technology study with a detailed description of the production, transport, installation, control, and care of concrete, and submit it to the Designer Engineer and the Engineer for approval. The Concrete Technology Study must also include all data and calculations for formwork and scaffolds that the Contractor will use during the performance of concrete works - Article 195 to 198 PBAB.

    - OTHER WORKS

      - QUALITY ASSURANCE

Work Description

Testing sewage pipes for water tightness according to the specified requirements.

Measurement and payment method

Paid per m’ of the tested pipeline.

      - TOPOGRAPHIC SURVEY

Work Description

Topographic survey of rainwater sewer will be performed after the completion  of sewer and before the backfilling of the trench: the positions of the inspection shafts and drains, their distances (lengths of the sections), the diameter of the pipes per sections, the dimension lines of bottom of the inspection shafts, as well as the bottom dimension lines and the diameters of all pipes placed in the inspection shaft.

Measurement and payment method

Paid per m’  of pipeline surveyed.

      - INSTALLATION FLUSHING

Work Description

Flushing the trench with the removal of all rough objects and dirt. Flushing is done by means of a tank.

Measurement and payment method

It is paid per m’ of the flushed trench.

      - AS-BUILT STATE STUDY

Work Description

Creation of As-built state study.

Measurement and payment method

It’s lump sum payment.